## Bill of Quantities
OpenMEP — Electrical Bill of Quantities (BOQ)
Project: Al Noor Mixed-Use Tower, Dubai, UAE ¦ Rev A ¦ 30 March 2026 ¦ Prepared by: Luquman A
Item | Description | Spec / Standard | Unit | Qty | Unit Rate (AED) | Total (AED) | Remarks | Ref
1.0 LV CABLES — MAIN DISTRIBUTION
1.1 | 4C+E 16mm² XLPE/SWA/PVC Cu BS 5467 | BS 7671 Table 4D5A Method C | m | 320 | 28.5 | 9120 | From LV board to DB-L2-01 | Cal-E-01
1.2 | 4C+E 25mm² XLPE/SWA/PVC Cu BS 5467 | BS 7671 Table 4D5A Method C | m | 180 | 42 | 7560 | LV board to AHU panels | Cal-E-02
1.3 | 4C+E 50mm² XLPE/SWA/PVC Cu BS 5467 | BS 7671 Table 4D5A Method C | m | 95 | 78 | 7410 | Main feeder to SMDB | Cal-E-03
1.4 | 4C+E 95mm² XLPE/SWA/PVC Cu BS 5467 | BS 7671 Table 4D5A Method C | m | 60 | 148 | 8880 | Utility connection feeder | Cal-E-04
2.0 LV SWITCHGEAR
2.1 | 800A 4P MCCB Icu=50kA | IEC 60947-2 DEWA approved | No. | 2 | 4200 | 8400 | Main MCCB in SMDB | Cal-E-05
2.2 | 250A 4P MCCB Icu=36kA | IEC 60947-2 | No. | 6 | 1650 | 9900 | Sub-distribution feeders | Cal-E-05
2.3 | 63A 4P MCCB Icu=25kA | IEC 60947-2 | No. | 18 | 480 | 8640 | Floor DBs | Cal-E-05
2.4 | 32A TP+N MCB Type C BS EN 60898 | BS EN 60898 | No. | 45 | 85 | 3825 | Final circuit protection | Cal-E-06
3.0 EARTHING & BONDING
3.1 | 25mm² bare Cu earth tape in GI conduit | BS 7671 Pt 5, IS 3043:2018 | m | 220 | 18 | 3960 | Main earth ring conductor | Cal-E-07
3.2 | Earth electrode 1800mm copper-bonded | BS 7430 | No. | 4 | 850 | 3400 | At MDB/generator | Cal-E-07
3.3 | 6mm² green-yellow CPC earth wire | BS 7671 Table 54.7 | m | 650 | 4.8 | 3120 | CPC in cable trays | Cal-E-07
4.0 LIGHTING SYSTEM
4.1 | LED panel 600×600 4000K 3500lm 32W | CIBSE LG7 >80Ra | No. | 120 | 380 | 45600 | Open office areas | Cal-L-01
4.2 | LED downlight 200mm 3000K 1200lm 15W | CIBSE LG7 | No. | 84 | 195 | 16380 | Corridors & lobbies | Cal-L-01
4.3 | LED emergency fitting 3hr NM BS EN 60598 | BS 5266 Part 1 | No. | 36 | 420 | 15120 | Emergency escape routes | Cal-L-02
5.0 CONTAINMENT SYSTEMS
5.1 | Cable tray 300mm×50mm GI BS EN 61537 | BS EN 61537 | m | 480 | 38 | 18240 | Main cable routes | —
5.2 | Cable tray 150mm×50mm GI BS EN 61537 | BS EN 61537 | m | 320 | 24 | 7680 | Branch routes | —
5.3 | 20mm GI conduit | BS EN 61386 | m | 1200 | 8.5 | 10200 | Final circuits | —
TOTAL (Excl. VAT)
VAT @ 5% (UAE)
GRAND TOTAL (Incl. VAT)

## Cable Schedule
OpenMEP — Cable Schedule ¦ Electrical Distribution ¦ BS 7671:2018+A2:2022
Cct Ref | From | To | Load (kW) | PF | Ib (A) | Size mm² | Type | Method | Ca | Cg | It (A) | Iz (A) | VD%
DB-M-01 | SMDB | LDB-G-01 | 45 | 0.85 | 76.41 | 16 | XLPE/SWA Cu | C | 0.91 | 1 | 102 | 92.8 | 4.28
DB-M-02 | SMDB | LDB-G-02 | 38 | 0.85 | 64.52 | 16 | XLPE/SWA Cu | C | 0.91 | 1 | 102 | 92.8 | 3.62
DB-M-03 | SMDB | LDB-L1-01 | 62 | 0.9 | 99.67 | 25 | XLPE/SWA Cu | C | 0.91 | 1 | 133 | 121 | 3.18
DB-M-04 | SMDB | AHU-01 | 75 | 0.9 | 120.56 | 35 | XLPE/SWA Cu | C | 0.91 | 1 | 163 | 148.3 | 2.87
DB-M-05 | SMDB | LIFT-01 | 55 | 0.9 | 88.41 | 25 | XLPE/SWA Cu | C | 0.91 | 1 | 133 | 121 | 2.54
DB-M-06 | SMDB | DB-EMERG | 30 | 0.85 | 50.94 | 16 | XLPE/SWA Cu | E | 1 | 1 | 117 | 117 | 1.97
DB-M-07 | SMDB | PUMP-FW | 22 | 0.85 | 37.36 | 10 | XLPE/SWA Cu | C | 0.91 | 1 | 77 | 70.1 | 2.13
DB-M-08 | SMDB | PUMP-CH | 18 | 0.85 | 30.57 | 10 | XLPE/SWA Cu | C | 0.91 | 1 | 77 | 70.1 | 1.74

## Standards Reference
OpenMEP — Standards Data Reference ¦ XLPE/Cu Ratings & Correction Factors
BS 7671 Table 4D5A — XLPE/Cu Multicore Ampacity (Amps)
Size (mm²) | A1 | B1 | C | D1 | E
1.5 | 17.5 | 20 | 26 | 22 | 29
2.5 | 24 | 27 | 34 | 29 | 39
4 | 32 | 36 | 46 | 38 | 52
6 | 40 | 46 | 57 | 47 | 65
10 | 54 | 63 | 77 | 63 | 88
16 | 73 | 85 | 102 | 83 | 117
25 | 95 | 110 | 133 | 107 | 152
35 | 117 | 135 | 163 | 130 | 187
50 | 141 | 163 | 198 | 154 | 227
70 | 179 | 207 | 253 | 194 | 290
95 | 216 | 250 | 306 | 233 | 352
120 | 249 | 288 | 354 | 269 | 406
150 | 285 | 330 | 407 | 306 | 464
185 | 324 | 376 | 464 | 349 | 530
240 | 380 | 442 | 546 | 408 | 624
300 | 435 | 507 | 628 | 466 | 717
400 | 510 | 594 | 754 | 551 | 856
630 | 680 | 792 | 1005 | 741 | 1151
BS 7671 Table 4B1 — Ambient Temperature Correction Factors (Ca) for XLPE
Temp (°C) | Ca Factor |  | Grouping (Cg) | No. Circuits | Touching
10 | 1.15 |  |  | 1 | 1
15 | 1.12 |  |  | 2 | 0.8
20 | 1.08 |  |  | 3 | 0.7
25 | 1.04 |  |  | 4 | 0.65
30 | 1 |  |  | 5 | 0.6
35 | 0.96 |  |  | 6 | 0.57
40 | 0.91 |  |  | 7 | 0.54
45 | 0.87 |  |  | 8 | 0.52
50 | 0.82 |  |  | 9 | 0.5
55 | 0.76 |  |  | 12 | 0.45
60 | 0.71 |  |  | 16 | 0.41
65 | 0.65 |  |  | 20 | 0.38
70 | 0.58
75 | 0.5
80 | 0.41
Generated by OpenMEP v1.0 · © 2025 Luquman A · github.com/kakarot-oncloud/openmep · 30 March 2026